Typical Specification

Three-Phase Solid Dielectric Multiway Switch with Automatic Transfer Package (ATC)

PAD MOUNT FRONT ACCESS STYLE

Part 1-GENERAL

  - DESCRIPTION

The switch shall consist of a solid dielectric insulated load break switches and resettable vacuum fault interrupter electronically controlled.  The switch shall be controlled by an ATC-451 Automatic Transfer Control Package

  - QUALITY ASSURANCE

- Manufacturer Qualifications:  The chosen manufacturer shall have at least 10 years experience in manufacturing solid dielectric insulated medium voltage switchgear. The manufacturer shall be completely and solely responsible for the performance of the fault interrupter as rated.

- The manufacturer shall furnish certification of ratings of the switch upon request.

- The switch shall comply with requirements of the latest revision of applicable industry standards, including:

IEEE C37.74, IEEE C37.60, ANSI/IEEE 386, IEC60529, IEEE 592,  ANSI/ IEEE C37.60.2 or equivalent, C37.60.1 or equivalent, IEC 60255-22, IEC 60255-21-1 or equivalent, IEC 60255-21-2 or equivalent

- The switch shall be tested to IEC 60529 for submersibilty.  The switch shall be rated IP68 for 20 days with a 20 foot head of water.

- The switch manufacturer shall be ISO 9001 and 14001 certified.

- The switch shall be RUS approved

  - DELIVERY, STORAGE, AND HANDLING

- The switch shall be shipped preassembled at the factory. No field assembly shall be required.

- The contractor, if applicable, shall handle, transfer and move the switches in accordance with manufacturer’s recommendations.

- Temperature Ranges

  - Storage and Operational without Batteries:  -40C to 70C

  - Operational (with Batteries):  -20C to 70C

PART 2-PRODUCTS

2.1 SWITCH CONFIGURATION

- Each switch shall be equipped with 3-phase Trident-SR load break switch ways and 3-phase Trident-S or Trident-ST fault interrupter ways, as indicated on the one-line diagram

- The switch shall be designed for front access to cables and operators

  - SWITCH CONSTRUCTION

- The switch shall be a dead-front design.  The operating mechanism housing shall be stainless steel with a viewing window for verification of vacuum interrupter contact position.  The mechanism housing shall be painted ANSI 70 light gray using corrosion-resistant epoxy paint.  Operating handles shall be padlockable and adaptable to keylock schemes.  The operating shaft shall be stainless steel providing maximum corrosion resistance. A double "O" ring shaft seal shall be used for a leak resistant, long life seal.

- The solid dielectric modules must be coated with a semi-conductive layer of epoxy, providing a completely dead front device.  The semi-conductive layer must be tested to IEEE 592 to ensure it can carry fault current to ground so as to ensure operator safety.

- The switch shall be designed for long term operation in the harshest environments.  The interrupter design must be tested to IEC60529 and achieve a protection rating of IP68, subjected to a 20’ head of water pressure for 20 days.

- The switch shall interrupt all load and fault currents within the vacuum bottle.

- Each switch mechanism shall consist of three individual vacuum bottle assemblies mechanically linked to an operating mechanism.

- The load break ways shall be G&W Trident-SR 3-phase switch.  The Trident-SR utilizes a magnetic actuator for high speed switch.  The magnetic actuator must be sealed within the mechanism housing.  No motors or external linkages to operate the load break switch shall be permitted.

- The fault interrupter ways shall be configured as follows (the specifier must choose)

____ Trident-S for 3-phase trip and reset

____ Trident-S w/ SafeVu for 3-phase trip and reset with integrated visible break (Up to 29.3kV only)

____ Trident-ST for 1 or 3-phase trip and reset

____ Combination as per provided three-line diagram (specifier must provide three-line diagram identifying each way)

2.3 DESIGN RATINGS

- Switch Ratings

The switch shall be rated (choose appropriate column):

| SELECTION OF RATINGS | IEEE/IEC |  |  |  |
| --- | --- | --- | --- | --- |
| Maximum Design Voltage, kV | 15.5 | 27 | 29.3 | 38 |
| Impulse Level (BIL) Voltage, kV | 110† | 125 | 125 | 150 |
| Continuous Current, Amperes | 630* | 630* | 630* | 630* |
| Load break Current, Amperes | 630* | 630* | 630* | 630* |
| One Minute Withstand (dry), AC kV | 35 | 60 | 60 | 70 |
| Production Test Rating | 34 | 40 | 40 | 50 |
| 15 Minute Withstand, DC kV | 53 | 78 | 78 | 103 |
| Momentary Current, kA asymmetrical | 20** | 20 | 20 | 20 |
| Fault Close Current, kA asymmetrical | 20** | 20 | 20 | 20 |
| Fault Interrupter rating, kA asymmetrical | 20** | 20 | 20 | 20 |
| Fault Interrupter rating, kA symmetrical | 12.5** | 12.5 | 12.5 | 12.5 |
| Mechanical Endurance, Operations | 2000 | 2000 | 2000 | 2000 |

* Non-SafeVu models available up to 800A continuous and load break rating upon request

*  15kV Trident-S switches have optional 16kA symmetrical (25.6kA asymmetrical) fault interrupt rating

† 15.5kV SafeVu rating is 95kV BIL

IEEE C37.60 Fault Interrupting Duty for 12.5kA sym. rating

| Percent of Maximum Interrupting Rating | Approximate Interrupting: Current, Amps | No. of Fault: Interruptions |
| --- | --- | --- |
| 15-20% | 2000 | 44 |
| 45-55% | 6000 | 56 |
| 90-100% | 12500 | 16 |
| Total Number of Fault Interruptions: 116 |  |  |

2.4 CABLE ENTRANCES

- Load Break Switches

Cable entrances shall be tested to IEEE 386 and be, as indicated on the switch drawing:

____15.5/27kV 125kV BIL Dead break Apparatus Bushings per IEEE 386 Figure 11 equipped with integral voltage sensing

____38kV 150kV BIL Dead break Apparatus Bushings per IEEE 386 Figure 11 equipped with integral voltage sensing

- Fault interrupters

Cable entrances shall be tested to IEEE 386 and be, as indicated on the switch drawing:

____15.5/27kV 125kV BIL Dead break Apparatus Bushings per IEEE 386 Figure 11

____15.5/27kV 125kV BIL 200A Bushing Well per IEEE 386 Figure 3

____38kV 150kV BIL Dead break Apparatus Bushings per IEEE 386 Figure 13

____38kV 150kV BIL 200A Bushing Well per IEEE 386 Figure 3

2.5 AUTOMATIC TRANSFER CONTROL (ATC-451)

    - Product Construction

      - Enclosure shall be NEMA 4 (mild steel) enclosure

      - Power supply

        - Requires 120VAC, 240VAC, 24VDC, 48Vdc, or 125VDC control power for operation.

        - Power supply shall include battery test (control sends a battery test command either via included programmable timer or specific customer request).  AC power and battery status are displayed on the front panel (for 120VAC or 240VAC power supply only).

      - Display - The ATC-451 shall have a display and LEDs that are used to show whether the  control is in manual or automatic mode, the position of the two source switches (open or close) as well as several messages.  The messages shall be used to inform the user of the current system status if the ATS control is timing for an operation.

      - Communication Ports - the ATC-451 shall have two communications ports for dedicated relay-to-relay communications.

        - One serial port pre-programmed for use with DNP3.0 Level 2.

        - The ATC-451 shall include three independent EIA-232 serial ports for external communications

      - Environment. The ATC-451 shall be suitable for continuous operation over a temperature range of –40° to +80°C.

    - Product Features

      - The microprocessor-based ATC-451 shall provide control, automation, monitoring, fault locating, and protection. The number of switched ways shall be indicated on the single line diagram. The control shall include self-checking functions shall be included. Specific requirements are as follows:

        - Programming – the ATC-451 shall be programmed using SEL AcSELerator software.  A copy of this software shall be included with the control.  Programmable templates shall also be included to allow modification of the basic transfer and protective settings listed in section 2.4 OPERATION.

        - Overcurrent Fault Protection. The ATC-451 shall incorporate selectable operating quantity time-overcurrent elements for load ways.

        - Password Protection. The ATC-451 shall have multilevel passwords to safeguard ATS control, protection, and automation settings.

        - Communication –device communication capability shall include Distributed Network Protocol (DNP). The ATC-451 shall incorporate certified DNP3 Level 2 Slave protocol.

        - Event Reporting and Sequential Events Recorder - The ATC-451 shall have the ability to automatically record disturbance events of up to 2 seconds at 8 kHz sampling rate and 5 seconds at 1 kHz sampling rate. Events shall be stored in nonvolatile memory. The relay shall also include a Sequential Events Recorder (SER) that stores the latest 1000 entries. The ATC-451 shall time-tag event reports to an absolute accuracy of 10 µs.

      - The control shall include the following front panel interface features:

        - Open/Close pushbuttons for each switched way.

        - Trip pushbuttons for each fault interrupting way

        - Local, Automatic, and/or Test mode enable/disable pushbuttons.

        - LED indication of Source switch status.  Open to be shown as Green, and Closed to be shown as Red.

        - LED indication of health of the Source

        - LED indication for cause of overcurrent trip of fault interrupting way(s)

        - LED indication of a malfunction and/or blocked condition

    - Operation of the ATC451 Package

      - Programming of the following Control and Timing functions shall be included as part of the Auto Transfer package and be settable through the provided programming templates.

        - Source 1 Initial Transfer Time - time between loss of Source 1 voltage and initiation of transfer to Source 2.

        - Source 1 Return Transfer Time - time after Source 1 returns to stable voltage before setting it as the preferred source.

        - Source 2 Initial Transfer Time – time between loss of Source 2 voltage and initiation of transfer to Source 1.

        - Source 2 Return Transfer Time – time after Source 2 returns to stable voltage before setting it as the preferred source.

        - Return Transfer Interruption Delay – time between operations on a return to preferred source transfer.

        - Preferred Source Operation – one of the sources can be selected as preferred.  The ATC-451 will always try to return to the preferred source when voltage is stabilized.

        - Source paralleling (yes or no)

        - Initial Transfer Sequence (open before close, close before open)

        - Return Transfer Sequence (open before close, close before open)

        - Generator as Alternate – The user will have the ability to set the alternate source as a generator. In this case, when the preferred source is lost and the initial transfer delay timer has expired, the control will activate (close) the Generator Start Contact. This contact will be connected to the generator. Once the generator is up and running, its voltage sensors will activate as a good source. The control will then initiate the transfer from the utility source to the generator alternate source. Once the preferred source returns and the return transfer delay timer expires, the control will initiate the return transfer to the preferred source; and begin the Generator Cool Down Timer. When the timer expires, the control will activate the Generator Stop Contact.

        - Generator Cool Down (only if Generator as Alternate is selected) – time after the return to preferred source before closing the generator stop contact.

        - Generator Stop Pulse Duration (only if Generator as Alternate is selected) – time that the generator stop contact should remain closed.

        - Ability to Open source ways of the switch(es) if both sources are lost with a user selectable time delay to ensure both sources are lost.

        - Ability to automatically reset a faulted condition alarm on the Source ways.

      - Programming the following Overcurrent functions shall be included as part of the ATS package and be settable for each load way through the provided programming templates:

        - Optional activation of single phase protection or option to activate 3-phase protection for a tap and single phase protection on another tap

        - Option to block the trip signal output contact on overcurrent trips for the load ways.

        - Current Transformer Secondary value for 50P Instantaneous trip.

        - Current Transformer Secondary value for 51P Phase Time overcurrent trip.

        - Time current curve selection for 51P protection.

        - Time dial for customization of 51P time current curve.

        - Current Transformer Secondary value for 50G Instantaneous Overcurrent trip on Phase Imbalance.

        - Current Transformer Secondary value to begin timing for 51G Phase Time Overcurrent trips due to phase imbalance.

        - Time current curve selection for 51G protection.

        - Time dial for customization of 51G time current curve.

        - Optional Maintenance Settings which allow for tighter settings to be applied by the user during specific time periods. These settings are in addition to the primary over current functions.

      - The following Operating Modes shall be part of the standard ATC-451 package

        - Local Operation Mode shall override any other mode. In Local Mode the operator shall have sole control over the switch(s). The pushbuttons on the front display panel shall be capable of operating both switch 1 and switch 2.  Settings changes shall be made only while the control is in the Local Operation Mode. The control shall not respond to the automatic transfer logic or SCADA commands while in Local Operation Mode.  The control shall not be able to initiate a transfer on voltage loss while the ATC-451 is in Local Operation Mode.

        - Automatic (Auto) Operation Mode shall cause the automatic transfer logic and the settings to be enabled. In Automatic Operation Mode the ATS shall act on its own to initiate a transfer if source voltages are lost. An LED next to the “AUTO MODE’ push button on the front control panel shall illuminate when the ATS is set to Automatic Operation Mode for clear visual indication to operators.  The preferred/alternate scheme the normal state of the control is to have the Preferred Source closed and the Alternate Source open. If power is lost to the Preferred Source for a period of time greater than that selected Initial Transfer Time delay, the control shall initiate a transfer to the Alternate Source if the Alternate Source is live. When the Preferred Source returns for a period of time greater than that selected for the Return Time delay, the control shall initiate a return transfer to the Preferred Source. If the Return Transfer Interruption Timer is activated it shall delay the Preferred Source’s operation. If the Alternate Source is lost before the Preferred Source returns, the control shall initiate emergency return logic which shall set the return delay timer to 0 and proceeds with the return transfer (including the Return Transfer Interruption delay). In the Non-Preferred scheme, the normal state of the control is to have a live source feeding the load. A transfer shall be initiated only if the source feeding the load is lost for a period of time greater than that selected for its transfer time delay, and the alternate source is live.

        - Remote Mode shall allow the SCADA system to issue operational commands (open/close) to both switch 1 and 2.  The control shall not be able to initiate a transfer on voltage loss while the ATC-451 is in Remote Mode.

        - Test Mode shall mean that the ATC-451 is in state where the user can verify logic settings, use simulated position inputs, and the option to operate actuators, Test Mode shall be available by first putting the ATC-451 into Local Mode and then pressing a button on the front panel titled “TEST MODE.”  From Test Mode the operator can verify the operation of the actuators and the timing of the transfer scheme.

        - Optional Blocked Condition shall mean the user can prevent the ATS from operating in manual or automatic mode until the conditions causing the block are removed or reset.  The following conditions shall cause the ATC-451 to enter a blocked state:

          - Source 1 or 2 status is invalid - shows both open and closed indication or no indication at all

          - Low Dielectric Condition – can only be removed if condition is removed (SF6 switches only)

          - Fault Block - An over current fault has occurred and has not been cleared

    - ATC451 Options (specifier to choose which options are required)

      - The following enclosure options shall be available

        - NEMA 4X (stainless steel) enclosure

        - Padlocking handle

        - Document holder inside of enclosure door

        - 120 VAC outlet for programming laptop power

        - Submersible enclosure rated IP68 (20’ head of water for 20 days) with NEMA 6P battery enclosure

          - Viewing windows for NEMA 6P lid

          - External Open/Close/ Power handles for NEMA 6P

          - Serial DNP 3.0 communication port available external to the enclosure

      - Dual input power supply and removal of battery option (for 120VAC or 240VAC power supply only)

      - Interface port for either a standard or high-accuracy demodulated IRIG-B time-synchronization input signal.

      - Ethernet connection using 10/100Base-T or 100Base-FX.

      - Ethernet DNP3 LAN/WAN communications capability.

      - IEC 61850. The relay shall provide IEC 61850-compliant communications. The IEC 61850 capability shall include GOOSE messaging and defined logical node data points.

      - Live Test Key – The ATC-451 shall include a test key that when activated will cause the ATC-451 to operate as if the preferred source has been lost.  The control will perform all normal times and operate the switches to the new alternate feeding position.  When the test key is returned to the normal position, the control will respond as if the preferred source has return and act according to the pre-programmed scenario.  The Live Test Key activation will be documented in the Sequence of Events Report and will appear in the DNP status.

      - Communication Equipment:  The following communication equipment will be included with the control: (user to choose one)

        - None

        - Power, data cable, and antenna protector/ feedthru for user defined and installed radio, Manufacturer _________ and Part Number ___________.

        - Or Power, data cable, and antenna protector/ feedthru for Sensus Telemetric DNP-RTMII-GSM.

        - Or Power, data cable, and antenna protector/feedthru for GE MDS 9710 radio with the following part number _______________.

        - Or Power, data cable, antenna protector/ feedthru and Sensus Telemetric DNP-RTMII-GSM with factory testing of the Sensus Telemetric communication.

        - Or included RS232/Fiber Optic transceivers for:

          - Single Mode fiber

            - Distance <23km OR 16 – 80km OR 16-110km  (user to choose one)

          - Multi Mode fiber with

            - V-Pin OR ST Pin (user to choose one)

            - for use with 650nm OR 850nm fiber (user to choose one)

            - over ______ distance.

2.6 PAD MOUNT ENCLOSURE

The enclosure shall be fabricated of 12 gauge galvanized steel and manufactured to ANSI C37.72 and C57.12.28 standards.  The enclosure shall be tamper resistant incorporating hinged access doors with pentahead locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

2.7 FACTORY PRODUCTION TESTS

Each interrupter shall undergo the following production testing.  Test reports must be available upon request

- A mechanical operation check

- AC hi-pot tested one minute phase-to-phase, phase-to-ground and across the open contacts

- Circuit resistance shall be checked.

- Each solid dielectric module shall undergo an X-ray inspection and a partial discharge test to ensure void-free construction.

- Leak test to insure the integrity of all seals and gaskets

- Primary current injection test to test CTs, trip mechanism, and electronic control

2.8 STANDARD COMPONENTS

The following shall be included as standard:

- Welded stainless steel mechanism housing painted light gray with stainless steel and brass fasteners.

- Lifting provisions

- ½”-13 nuts to provide sufficient grounding provisions for interrupter and all cable entrances.

- Stainless steel three line diagram and corrosion-resistant nameplates.

- Switch operating handle with padlock provision.

- Removable parking stands

- Mounting bracket

- Operating handles

2.9 OPTIONS

(Choose as necessary for the application)

The following options shall be supplied:

- Mounting frame to bolt switch to the floor (specify galvanized or stainless steel construction.  Specify height of lowest bushing)

- 800A continuous and load break rating

- Field replaceable bushings for the fault interrupters

- 4/0 brass ground lugs

- Provisions to mount a  key interlock after installation

- Form C contacts for remote monitoring of the position of the fault interrupter contacts.

- 12-gauge stainless steel enclosure manufactured to ANSI C37.72 and C57.12.29 standards.  The enclosure shall be tamper resistant incorporating hinged access doors with penta head locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

2.10 LABELING

A. Hazard Alerting Signs

The exterior of the pad mount enclosure (if furnished) shall be provided with “Warning--Keep Out--Hazardous Voltage Inside--Can Shock, Burn, or Cause Death” signs. Each unit of switchgear shall be provided with a “Danger--Hazardous Voltage--Failure to Follow These Instructions Will Likely Cause Shock, Burn, or Death” sign. The text shall further indicate that operating personnel must know and obey the employer’s work rules, know the hazards involved, and use proper protective equipment and tools to work on this equipment. Each unit of switchgear shall be provided with a “Danger--Keep Away--Hazardous Voltage--Will Shock, Burn, or Cause Death” sign.

B.  Nameplates, Ratings Labels, and Connection Diagrams

Each unit of switchgear shall be provided with a nameplate indicating the manufacturer’s name, catalog number, model number, date of manufacture, and serial number. Each unit of switchgear shall be provided with a ratings label indicating the following: voltage rating; main bus continuous rating; short-circuit rating; fault interrupter ratings including interrupting and duty-cycle fault-closing; and fault interrupter switch ratings including duty-cycle fault-closing and short-time.